## Slide 1
Surface Seal
(Sand Cement Slurry)
30” Borehole
Est. Water Level
~120 feet
Land surface
36” (OD) LCS conductor,
A53B, 0.375-inch wall thickness
2’ conductor stickup
0’
48” Borehole
Bentonite Seal
1,000’
39’
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 Sounding Tube (blank tubing), 0.154” wall thickness, +1 to 125 ft.
20” (OD) ASTM 139 Grade B (LCS)
0.375” wall thickness, 0.060” wide slots
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 with bottom cap, 0.154” wall thickness, perforated (0.050” wide mill slots) 125 to 800 ft.
Neat Cement Seal
125’
REPLACEMENT WELL DESIGN
TYPICAL 1000’ DESIGN - 20” CASING
ROOSEVELT IRRIGATION DISTRICT
Figure
1
Maricopa County, Arizona
3.5” (OD), 3.026” (ID), ASTM A53 Grade B (LCS) Sch. 40 Gravel Feed Tube, 0.237” wall thickness, Open-ended on bottom, +1 to 105 ft
995’
20” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness with Bull Nosed bottom.
August 2024 Project 24-0527
70’
100’
105’
820’
800’
20” (OD) ASTM 139
Grade B (LCS) Well Casing,
0.375” wall thickness.
Transition Sand 20 x 40
90’
20” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness.
Tacna Sand 6 x 16
(100-1,000 ft)
Notes:
Drawing Not to Scale
Depths are below land surface unless noted
Centralizers installed at intervals no more
than 50 feet
OD – Outside diameter
ID – Inside diameter
LCS – Low carbon steel
Sch. 40 - Schedule 40

## Slide 2
Surface Seal
(Sand Cement Slurry)
30” Borehole
Est. Water Level
~120 feet
Land surface
36” (OD) LCS conductor,
A53B, 0.375-inch wall thickness
2’ conductor stickup
0’
48” Borehole
Bentonite Seal
800’
39’
20” (OD) ASTM 139 Grade B (LCS)
0.375” wall thickness, 0.060” wide slots
Neat Cement Seal
125’
REPLACEMENT WELL DESIGN
TYPICAL 800’ DESIGN - 20” CASING
ROOSEVELT IRRIGATION DISTRICT
Figure
2
Maricopa County, Arizona
795’
20” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness with Bull Nosed bottom.
August 2024 Project 24-0527
70’
100’
105’
620’
600’
20” (OD) ASTM 139
Grade B (LCS) Well Casing,
0.375” wall thickness.
Transition Sand 20 x 40
90’
20” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness.
Tacna Sand 6 x 16
(100-800 ft)
Notes:
Drawing Not to Scale
Depths are below land surface unless noted
Centralizers installed at intervals no more
than 50 feet
OD – Outside diameter
ID – Inside diameter
LCS – Low carbon steel
Sch 40 - Schedule 40
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 Sounding Tube (blank tubing), 0.154” wall thickness, +1 to 125 ft.
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 with bottom cap, 0.154” wall thickness, perforated (0.050” wide mill slots) 125 to 600 ft.
3.5” (OD), 3.026” (ID), ASTM A53 Grade B (LCS) Sch. 40 Gravel Feed Tube, 0.237” wall thickness, Open-ended on bottom, +1 to 105 ft

## Slide 3
Surface Seal
(Sand Cement Slurry)
30” Borehole
Est. Water Level
~120 feet
Land surface
36” (OD) LCS conductor,
A53B, 0.375-inch wall thickness
2’ conductor stickup
0’
48” Borehole
Bentonite Seal
700’
39’
20” (OD) ASTM 139 Grade B (LCS)
0.375” wall thickness, 0.060” wide slots
Neat Cement Seal
125’
REPLACEMENT WELL DESIGN
TYPICAL 700’ DESIGN - 20” CASING
ROOSEVELT IRRIGATION DISTRICT
Figure
3
Maricopa County, Arizona
695’
20” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness with Bull Nosed bottom.
August 2024 Project 24-0527
70’
100’
105’
520’
500’
20” (OD) ASTM 139
Grade B (LCS) Well Casing,
0.375” wall thickness.
Transition Sand 20 x 40
90’
20” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness.
Tacna Sand 6 x 16
(100-700 ft)
Notes:
Drawing Not to Scale
Depths are below land surface unless noted
Centralizers installed at intervals no more
than 50 feet
OD – Outside diameter
ID – Inside diameter
LCS – Low carbon steel
Sch 40 - Schedule 40
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 Sounding Tube (blank tubing), 0.154” wall thickness, +1 to 125 ft.
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 with bottom cap, 0.154” wall thickness, perforated (0.050” wide mill slots) 125 to 500 ft.
3.5” (OD), 3.026” (ID), ASTM A53 Grade B (LCS) Sch. 40 Gravel Feed Tube, 0.237” wall thickness, Open-ended on bottom, +1 to 105 ft

## Slide 4
Surface Seal
(Sand Cement Slurry)
34” Borehole
Est. Water Level
~120 feet
Land surface
42” (OD) LCS conductor,
A53B, 0.375-inch wall thickness
2’ conductor stickup
0’
48” Borehole
Bentonite Seal
1,000’
39’
Tacna Sand 6 x 16
(100-1,000 ft)
24” (OD) ASTM 139 Grade B (LCS)
0.375” wall thickness, 0.060” wide slots
Neat Cement Seal
125’
Notes:
Drawing Not to Scale
Depths are below land surface unless noted
Centralizers installed at intervals no more
than 50 feet
REPLACEMENT WELL DESIGN
TYPICAL 1000’ DESIGN - 24” CASING
ROOSEVELT IRRIGATION DISTRICT
Figure
4
Maricopa County, Arizona
995’
24” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness with Bull Nosed bottom.
OD – Outside diameter
ID – Inside diameter
LCS – Low carbon steel
Sch 40 - Schedule 40
August 2024 Project 24-0527
70’
100’
105’
820’
800’
24” (OD) ASTM 139
Grade B (LCS) Well Casing,
0.375” wall thickness.
Transition Sand 20 x 40
90’
24” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness.
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 Sounding Tube (blank tubing), 0.154” wall thickness, +1 to 125 ft.
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 with bottom cap, 0.154” wall thickness, perforated (0.050” wide mill slots) 125 to 800 ft.
3.5” (OD), 3.026” (ID), ASTM A53 Grade B (LCS) Sch. 40 Gravel Feed Tube, 0.237” wall thickness, Open-ended on bottom, +1 to 105 ft

## Slide 5
Surface Seal
(Sand Cement Slurry)
34” Borehole
Est. Water Level
~120 feet
Land surface
42” (OD) LCS conductor,
A53B, 0.375-inch wall thickness
2’ conductor stickup
0’
48” Borehole
Bentonite Seal
800’
39’
Tacna Sand 6 x 16
(100-800 ft)
24” (OD) ASTM 139 Grade B (LCS)
0.375” wall thickness, 0.060” wide slots
Neat Cement Seal
125’
Notes:
Drawing Not to Scale
Depths are below land surface unless noted
Centralizers installed at intervals no more
than 50 feet
REPLACEMENT WELL DESIGN
TYPICAL 800’ DESIGN - 24” CASING
ROOSEVELT IRRIGATION DISTRICT
Figure
5
Maricopa County, Arizona
795’
24” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness with Bull Nosed bottom.
OD – Outside diameter
ID – Inside diameter
LCS – Low carbon steel
Sch 40 - Schedule 40
August 2024 Project 24-0527
70’
100’
105’
620’
600’
24” (OD) ASTM 139
Grade B (LCS) Well Casing,
0.375” wall thickness.
Transition Sand 20 x 40
90’
24” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness.
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 Sounding Tube (blank tubing), 0.154” wall thickness, +1 to 125 ft.
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 with bottom cap, 0.154” wall thickness, perforated (0.050” wide mill slots) 125 to 600 ft.
3.5” (OD), 3.026” (ID), ASTM A53 Grade B (LCS) Sch. 40 Gravel Feed Tube, 0.237” wall thickness, Open-ended on bottom, +1 to 105 ft

## Slide 6
Surface Seal
(Sand Cement Slurry)
34” Borehole
Est. Water Level
~120 feet
Land surface
42” (OD) LCS conductor,
A53B, 0.375-inch wall thickness
2’ conductor stickup
0’
48” Borehole
Bentonite Seal
700’
39’
Tacna Sand 6 x 16
(100-700 ft)
24” (OD) ASTM 139 Grade B (LCS)
0.375” wall thickness, 0.060” wide slots
Neat Cement Seal
125’
Notes:
Drawing Not to Scale
Depths are below land surface unless noted
Centralizers installed at intervals no more
than 50 feet
REPLACEMENT WELL DESIGN
TYPICAL 700’ DESIGN - 24” CASING
ROOSEVELT IRRIGATION DISTRICT
Figure
6
Maricopa County, Arizona
695’
24” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness with Bull Nosed bottom.
OD – Outside diameter
ID – Inside diameter
LCS – Low carbon steel
Sch 40 - Schedule 40
August 2024 Project 24-0527
70’
100’
105’
520’
500’
24” (OD) ASTM 139
Grade B (LCS) Well Casing,
0.375” wall thickness.
Transition Sand 20 x 40
90’
24” (OD) ASTM 139 Grade B (LCS)
Well Casing, 0.375” wall thickness.
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 Sounding Tube (blank tubing), 0.154” wall thickness, +1 to 125 ft.
2.375” (OD), 2.067” (ID) ASTM A53 Grade B (LCS) Sch. 40 with bottom cap, 0.154” wall thickness, perforated (0.050” wide mill slots) 125 to 500 ft.
3.5” (OD), 3.026” (ID), ASTM A53 Grade B (LCS) Sch. 40 Gravel Feed Tube, 0.237” wall thickness, Open-ended on bottom, +1 to 105 ft